## MDF
ORG Vert | Spatiu ocupat in U | Denumire/ tip echipament | Model | Scurta descriere/ nr porturi | Putere electrica necesara W | Caldura disipata BTU | ORG Vert
Organizator de cabluri vertical | 2 | Firewall | FPR-1140 | Firewall pentru protectia retelei | 100 | 341.2 | Organizator de cabluri vertical
1
1
1
1
1
1
1
1
1
1
1
1
| 1 | Patch Pannel FO |  | 24 Porturi cu conectori LC
| 13 | Switch L3 | C9410R | Rutare și comutare la rețea.
|  | Power Supply | 9400 Series | Sursa putere 3200W AC | 3200 | 10918.4
|  | Organizer Orizontal |  |  | 0 | 0
| 2 | InRow RD, 300mm, Air Cooled |  | https://www.vertiv.com/en-us/products-catalog/thermal-management/in-row-cooling/liebert-crv-in-row-cooling-system-10-40kw/ | 4400
| 4 | UPS Eaton 5PX UPS Eaton 5PX https://www.eaton.com/ro/ro-ro/catalog/backup-power-ups-surge-it-power-distribution/eaton-5px-ups-emea.html 5000 | APC Smart-UPS 5000VA | https://www.apc.com/shop/hr/en/products/APC-Smart-UPS-5000VA-230V-Rackmount-Tower/P-SUA5000RMI5U | 5000
| 4 | UPS Eaton 5PX UPS Eaton 5PX https://www.eaton.com/ro/ro-ro/catalog/backup-power-ups-surge-it-power-distribution/eaton-5px-ups-emea.html 5000 | APC Smart-UPS 5000VA | https://www.apc.com/shop/hr/en/products/APC-Smart-UPS-5000VA-230V-Rackmount-Tower/P-SUA5000RMI5U | 5000
Total | 38 |  |  |  | 7700 | 11259.6
|  |  |  | Putere disponibila in UPS | 10000
[5 empty] | Consum electric AC | Racire AC
|  | InRow RD, 300mm, Air Cooled |  | https://www.vertiv.com/en-us/products-catalog/thermal-management/in-row-cooling/liebert-crv-in-row-cooling-system-10-40kw/ | 4400 | 34000
Sistemele de racire sunt conectate cu un furtun la exteriorul cladirii pentru disiparea caldurii
|  |  |  | Total | 4400 | 34000
|  | Nr prize simple de conectat la acest DF, valoarea se ia din etapa 2 | 188
|  | Nr prize disponibil in PP UTP in acest rack | 0 | Formula se modifica daca utilizati PP cu alt numar de prize, 24, 48 etc.
Note | Se lasa loc liber in Rack cca 10-20% din spatiu pentru dezvoltari ulterioare
Daca nu incape intrun singur Rack se pot pune mai multe in fieacre DF, UPS /uri se pun in fiecare Rack
Rack sunt de maxim 48 U sau 52 U inaltime
Puterea disponibila in UPS sa fie cu 30% mai mare decat total putere necesar
Daca sunt mai multe UPS-uri se distribuie sarcina intre ele
Capacitatea bateriilor/acumultorilor din UPS se determina in asa fel incat sa asigure o functionare de 30 la 60 minute la sarcina medie
Total porturi UTP din Switchuri intre 70 si 100 % din nr de prize simple care se conecteaza la un DF, functie de strategia aleasa
nr de porturi total din Patch Pannel UTP trebuie sa fie mai mare sau egal cu nr de prize simple care se conecteaza la un DF
Echipamentele de racire se pun in fiecare DF si vor trebuii sa aibe capacitatea de racire cu cca 30% mai mare decat total Caldura dispata
Echipamentele de racire, Aer Conditionat de uz industrial nu sunt alimentate din UPS
Foia de calcul se replica pentru fiecare DF in parte
Valorile din exemple sunt arbitrare si vor trebuii inlocuite cu date din fisa tehnica a echipamentelor alese pentru proiect

## IDF1
ORG Vert | Spatiu ocupat in U | Denumire/ tip echipament | Model | Scurta descriere/ nr porturi | Putere electrica necesara W | Caldura disipata BTU | ORG Vert
Organizator de cabluri vertical | 1 | Patch Pannel UTP |  | 48 UTP Cat6 |  |  | Organizator de cabluri vertical
| 1 | Patch Pannel UTP |  | 48 UTP Cat6
| 1 | Patch Pannel UTP |  | 48 UTP Cat6
| 1 | Patch Pannel UTP |  | 48 UTP Cat6
| 1 | Organizer Orizontal
| 1 | Supervisor | C9400-SUP-1 | Supervizor seria 9400
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
8
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
Organizer Orizontal
| 1 | Patch Pannel UTP |  | 48 UTP Cat6
|  | Patch Pannel UTP |  | 48 UTP Cat6
|  | Patch Pannel UTP |  | 48 UTP Cat6
|  | Patch Pannel UTP |  | 48 UTP Cat6
|  | Patch Pannel UTP |  | 48 UTP Cat6
|  | InRow RD, 300mm, Air Cooled |  | https://www.vertiv.com/en-us/products-catalog/thermal-management/in-row-cooling/liebert-crv-in-row-cooling-system-10-40kw/ | 4400
|  | UPS Eaton 5PX UPS Eaton 5PX https://www.eaton.com/ro/ro-ro/catalog/backup-power-ups-surge-it-power-distribution/eaton-5px-ups-emea.html 5000 | APC Smart-UPS 5000VA | https://www.apc.com/shop/hr/en/products/APC-Smart-UPS-5000VA-230V-Rackmount-Tower/P-SUA5000RMI5U | 5000
Total | 23 |  |  |  | 4832 | 1473.984
|  |  |  | Putere disponibila in UPS | 5000
[5 empty] | Consum electric AC | Racire AC
|  | InRow RD, 300mm, Air Cooled |  | https://www.vertiv.com/en-us/products-catalog/thermal-management/in-row-cooling/liebert-crv-in-row-cooling-system-10-40kw/ | 4400 | 34000
Sistemul de racire este conectat cu un furtun la sistemul de ventilatie pentru disiparea caldurii
|  |  |  | Total | 4400 | 34000
|  | Nr prize simple de conectat la acest DF, valoarea se ia din etapa 2 | 188
|  | Nr prize disponibil in PP UTP in acest rack | 384 | Formula se modifica daca utilizati PP cu alt numar de prize, 24, 48 etc.
Note | Se lasa loc liber in Rack cca 10-20% din spatiu pentru dezvoltari ulterioare
Daca nu incape intrun singur Rack se pot pune mai multe in fieacre DF, UPS /uri se pun in fiecare Rack
Rack sunt de maxim 48 U sau 52 U inaltime
Puterea disponibila in UPS sa fie cu 30% mai mare decat total putere necesar
Daca sunt mai multe UPS-uri se distribuie sarcina intre ele
Capacitatea bateriilor/acumultorilor din UPS se determina in asa fel incat sa asigure o functionare de 30 la 60 minute la sarcina medie
Total porturi UTP din Switchuri intre 70 si 100 % din nr de prize simple care se conecteaza la un DF, functie de strategia aleasa
nr de porturi total din Patch Pannel UTP trebuie sa fie mai mare sau egal cu nr de prize simple care se conecteaza la un DF
Echipamentele de racire se pun in fiecare DF si vor trebuii sa aibe capacitatea de racire cu cca 30% mai mare decat total Caldura dispata
Echipamentele de racire, Aer Conditionat de uz industrial nu sunt alimentate din UPS
Foia de calcul se replica pentru fiecare DF in parte
Valorile din exemple sunt arbitrare si vor trebuii inlocuite cu date din fisa tehnica a echipamentelor alese pentru proiect

## IDF...
ORG Vert | Spatiu ocupat in U | Denumire/ tip echipament | Model | Scurta descriere/ nr porturi | Putere electrica necesara W | Caldura disipata BTU | ORG Vert
Organizator de cabluri vertical | 1 | Patch Pannel UTP |  | 48 UTP Cat6 |  |  | Organizator de cabluri vertical
| 1 | Patch Pannel UTP |  | 48 UTP Cat6
| 1 | Patch Pannel UTP |  | 48 UTP Cat6
| 1 | Patch Pannel UTP |  | 48 UTP Cat6
| 1 | Organizer Orizontal
| 1 | Supervisor | C9400-SUP-1 | Supervizor seria 9400
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
| 1 | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
1
8
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
|  | Switch L2 | C1000-24T-4X-L | Cisco® Catalyst® 1000 Series Switches | 27 | 92.124
Organizer Orizontal
| 1 | Patch Pannel UTP |  | 48 UTP Cat6
|  | Patch Pannel UTP |  | 48 UTP Cat6
|  | Patch Pannel UTP |  | 48 UTP Cat6
|  | Patch Pannel UTP |  | 48 UTP Cat6
|  | InRow RD, 300mm, Air Cooled |  | https://www.vertiv.com/en-us/products-catalog/thermal-management/in-row-cooling/liebert-crv-in-row-cooling-system-10-40kw/ | 4400
|  | UPS Eaton 5PX | UPS Eaton 5PX | https://www.eaton.com/ro/ro-ro/catalog/backup-power-ups-surge-it-power-distribution/eaton-5px-ups-emea.html | 5000
|  | UPS Eaton 5PX | UPS Eaton 5PX | https://www.eaton.com/ro/ro-ro/catalog/backup-power-ups-surge-it-power-distribution/eaton-5px-ups-emea.html
Total | 23 |  |  |  | 4805 | 1381.86
|  |  |  | Putere disponibila in UPS | 5000
[5 empty] | Consum electric AC | Racire AC
|  | InRow RD, 300mm, Air Cooled |  | https://www.vertiv.com/en-us/products-catalog/thermal-management/in-row-cooling/liebert-crv-in-row-cooling-system-10-40kw/ | 4400 | 34000
Sistemul de racire este conectat cu un furtun la sistemul de ventilatie al cladirii pentru disiparea caldurii
|  |  |  | Total | 4400 | 34000
|  | Nr prize simple de conectat la acest DF, valoarea se ia din etapa 2 | 178
|  | Nr prize disponibil in PP UTP in acest rack | 360 | Formula se modifica daca utilizati PP cu alt numar de prize, 24, 48 etc.
Note | Se lasa loc liber in Rack cca 10-20% din spatiu pentru dezvoltari ulterioare
Daca nu incape intrun singur Rack se pot pune mai multe in fieacre DF, UPS /uri se pun in fiecare Rack
Rack sunt de maxim 48 U sau 52 U inaltime
Puterea disponibila in UPS sa fie cu 30% mai mare decat total putere necesar
Daca sunt mai multe UPS-uri se distribuie sarcina intre ele
Capacitatea bateriilor/acumultorilor din UPS se determina in asa fel incat sa asigure o functionare de 30 la 60 minute la sarcina medie
Total porturi UTP din Switchuri intre 70 si 100 % din nr de prize simple care se conecteaza la un DF, functie de strategia aleasa
nr de porturi total din Patch Pannel UTP trebuie sa fie mai mare sau egal cu nr de prize simple care se conecteaza la un DF
Echipamentele de racire se pun in fiecare DF si vor trebuii sa aibe capacitatea de racire cu cca 30% mai mare decat total Caldura dispata
Echipamentele de racire, Aer Conditionat de uz industrial nu sunt alimentate din UPS
Foia de calcul se replica pentru fiecare DF in parte
Valorile din exemple sunt arbitrare si vor trebuii inlocuite cu date din fisa tehnica a echipamentelor alese pentru proiect